## TARGET FORM
1. Client |  | Kye Garvin | [7 empty] | Job # | DOE20COT001
2. Sq. Ft of Unit |  | 1800 |  | 3. Ceiling Height |  |  | 8 | 4. Total Volume |  | 14400 | 5. ACH | 11
Readings from Initial Assessment
ACH | 2640 |  | MRV | 2037 |  | R. T. | 2520 | BTL | 1554 |  |  | TARGET
6. Initial BD CFM Reading |  |  |  | 3600 | cfm | @ | 50 | Pa | B/D Ring # |  | Open | 2037
7. Initial Total Duct Leakage |  |  |  | 446 | cfm | @ | 25 | Pa | D/B Ring # |  | 2 | 216
8. Initial WRTO Duct Leakage |  |  |  | 312 | cfm | @ | 25 | Pa | D/B Ring # |  | 2 | 144
1. Input the client name and job number.
2. Input the square footage of the home.
2.1. This should be the area inside the conditioned space and/or building envelope.
3. Input ceiling height.
3.1. If the ceiling is vaulted or different heights, use best judgment and determine an average ceiling height.
4. Total volume is calculated automatically.
5. Suggested ACH (Air Changes per hour) are calculated automatically.
6. Input the initial Blower Door CFM reading.
6.1. Input the pascals. This Should be 50.
6.2. Select the Blower Door ring used for the test. This is a drop-down menu (select arrow).
6.3. The After Weatherization Blower Door CFM target is automatically calculated. This is based on several formulas.
7. Input the initial Total Duct Leakage CFM.
7.1. Input the pascals. This Should be 25. This does not change the target.
7.2. Select the Duct Blaster ring used for the test. This is a drop down menu (select arrow).
7.3. The After Duct Sealing CFM target is automatically calculated @ 12 % of Ft2 of conditioned space.
8. Input the initial Outside Duct Leakage CFM.
8.1. Input the pascals. This should be 25. This does not change the target
8.2. Select the Duct Blaster ring used for the test. This is a drop-down menu (select arrow).
8.3. The After Duct Sealing CFM target is automatically calculated @ 8% of Ft2 of conditioned space.

## Reduction Formulas (hidden)
Old Formula |  |  |  | 1800 | 8 | 8.5 | 9 | 9.5 | 10
1599 | OAS |  |  | Volume | 14400 | 15300 | 16200 | 17100 | 18000
1600 | 0.75 | 1200 |  | 3 | 720 | 765 | 810 | 855 | 900
2750 | 0.75 | 2062.5 |  | 4 | 960 | 1020 | 1080 | 1140 | 1200
2751 | 0.7 | 1925.7 |  | 5 | 1200 | 1275 | 1350 | 1425 | 1500
4250 | 0.7 | 2975 |  | 6 | 1440 | 1530 | 1620 | 1710 | 1800
4251 | 0.6 | 2550.6 |  | 7 | 1680 | 1785 | 1890 | 1995 | 2100
5500 | 0.6 | 3300 |  | 8 | 1920 | 2040 | 2160 | 2280 | 2400
5501 | 0.55 | 3025.55 |  | 9 | 2160 | 2295 | 2430 | 2565 | 2700
7500 | 0.55 | 4125 |  | 10 | 2400 | 2550 | 2700 | 2850 | 3000
7501 | 0.5 | 3750.5 |  | 11 | 2640 | 2805 | 2970 | 3135 | 3300
|  |  |  | 12 | 2880 | 3060 | 3240 | 3420 | 3600
New Formula |  |  |  | 13 | 3120 | 3315 | 3510 | 3705 | 3900
1500 | 0.9 | 1350 |  | 14 | 3360 | 3570 | 3780 | 3990 | 4200
1501 | 0.75 | 1125.75 |  | 15 | 3600 | 3825 | 4050 | 4275 | 4500
2500 | 0.75 | 1875 | Old Formula
2501 | 0.7 | 1750.7 |  | BTL | 1554 | 1651.125 | 1748.25 | 1845.375 | 1942.5
4000 | 0.7 | 2800 | Initial BD | 1500 | 1527 | 1575.5625 | 1624.125 | 1672.6875 | 1721.25
4001 | 0.6 | 2400.6 |  | 2500 | 1714.5 | 1763.0625 | 1811.625 | 1860.1875 | 1908.75
5000 | 0.6 | 3000 |  | 3774 | 2097.9 | 2146.4625 | 2195.025 | 2243.5875 | 2292.15
7501 | 0.5 | 3750.5 |  | 4500 | 2127 | 2175.5625 | 2224.125 | 2272.6875 | 2321.25
|  |  |  | 5500 | 2427 | 2475.5625 | 2524.125 | 2572.6875 | 2621.25
|  |  |  | 6500 | 2564.5 | 2613.0625 | 2661.625 | 2710.1875 | 2758.75
|  |  |  | 7501 | 2652.25 | 2700.8125 | 2749.375 | 2797.9375 | 2846.5
New Formula
|  |  |  | BTL | 1554 | 1651.125 | 1748.25 | 1845.375 | 1942.5
|  |  | Initial BD | 1500 | 1452 | 1500.5625 | 1549.125 | 1597.6875 | 1646.25
|  |  |  | 2500 | 1714.5 | 1763.0625 | 1811.625 | 1860.1875 | 1908.75
|  |  |  | 3774 | 2097.9 | 2146.4625 | 2195.025 | 2243.5875 | 2292.15
|  |  |  | 4500 | 2127 | 2175.5625 | 2224.125 | 2272.6875 | 2321.25
|  |  |  | 5500 | 2152 | 2200.5625 | 2249.125 | 2297.6875 | 2346.25
|  |  |  | 6500 | 2402 | 2450.5625 | 2499.125 | 2547.6875 | 2596.25
|  |  |  | 7501 | 2652.25 | 2700.8125 | 2749.375 | 2797.9375 | 2846.5